## Wiring_Schedule
Wire_Tag | Source_Device | Source_Terminal | Dest_Device | Dest_Terminal | Expected_Color | Wire_Gauge_mm2 | Ferrule_ID | Signal_Type | Remarks
W-101 | QF1 | L1_OUT | QF2 | L_IN | Black | 2.5 | QF1:L1 | AC Power | EAGLE-DEMO-001 Phase 1 feed
W-102 | QF1 | L2_OUT | QF3 | L_IN | Black | 2.5 | QF1:L2 | AC Power | EAGLE-DEMO-001 Phase 2 feed
W-103 | QF2 | L_OUT | PS1 | L | Black | 1.5 | PS1:L | AC Power | Power supply AC input
W-104 | QF2 | N_OUT | PS1 | N | Light Blue | 1.5 | PS1:N | AC Neutral | Power supply AC neutral
W-105 | PS1 | +24V | PLC1 | L+ | Red | 1.5 | PLC1:24V | DC 24V | PLC main power feed
W-106 | PS1 | 0V | PLC1 | M | Dark Blue | 1.5 | PLC1:0V | DC Ground | PLC return ground
W-107 | PLC1 | DO_0 | K1 | A1 | Dark Blue | 0.75 | K1:A1 | Control | Motor 1 contactor coil
W-108 | K1 | A2 | X1 | 14 | Blue | 0.75 | X1:14 | Control | Motor 1 return to terminal X1:14
W-109 | PLC1 | DO_1 | K2 | A1 | Dark Blue | 0.75 | K2:A1 | Control | Motor 2 contactor coil
W-110 | K2 | A2 | X1 | 15 | Blue | 0.75 | X1:15 | Control | Motor 2 return to terminal X1:15
W-111 | KA1 | 13 | PLC1 | DI_0 | White | 0.75 | KA1:13 | Safety | Emergency stop monitoring
W-112 | KA1 | 14 | X1 | 18 | White | 0.75 | X1:18 | Safety | Emergency stop circuit return
W-113 | QF1 | PE | X1 | 6 | Green-Yellow | 4.0 | PE:X1-6 | Ground | Chassis protective ground
W-114 | SPD1 | PE | X1 | 6 | Green-Yellow | 4.0 | SPD:PE | Ground | Surge protective discharge

## BOM_List
Reference_Tag | Component_Type | Manufacturer | Part_Number | Rail_Designation | Qty
PS1 | Power Supply 24VDC 10A | Phoenix Contact | TRIO-PS-2G/1AC/24DC/10 | DIN 1 | 1
QF1 | Main Circuit Breaker 3P 63A | Schneider Electric | A9F74363 | DIN 1 | 1
QF2 | Miniature Circuit Breaker 1P 16A | Schneider Electric | A9F74116 | DIN 1 | 1
QF3 | Miniature Circuit Breaker 1P 10A | Schneider Electric | A9F74110 | DIN 1 | 1
SPD1 | Surge Protector Type 2 40kA | DEHN | 952070 | DIN 1 | 1
PLC1 | PLC CPU 1214C DC/DC/DC | Siemens | 6ES7214-1AG40-0XB0 | DIN 2 | 1
K1 | Motor Contactor 25A 24VDC | Siemens | 3RT2026-1BB40 | DIN 2 | 1
K2 | Motor Contactor 25A 24VDC | Siemens | 3RT2026-1BB40 | DIN 2 | 1
KA1 | Safety Relay Module | Pilz | PNOZ s4 24VDC | DIN 2 | 1
X1 | Terminal Block Strip 20P | Weidmuller | WDU 2.5 | DIN 3 | 20

## Terminal_Plan
Terminal_Strip | Terminal_No | Function_Designation | Wire_Connected | Signal_Level | Wire_Color
X1 | 1 | Main Phase L1 Infeed | W-101 | 400VAC | Black
X1 | 2 | Main Phase L2 Infeed | W-102 | 400VAC | Black
X1 | 3 | Main Phase L3 Infeed | W-100 | 400VAC | Black
X1 | 4 | System Neutral Return | W-104 | 0VAC | Light Blue
X1 | 5 | Aux Neutral Return | W-104B | 0VAC | Light Blue
X1 | 6 | Protective Earth Bond | W-113 | PE | Green-Yellow
X1 | 14 | Motor 1 Contactor K1 Return | W-108 | 0VDC | Blue
X1 | 15 | Motor 2 Contactor K2 Return | W-110 | 0VDC | Blue
X1 | 18 | Emergency Stop Return | W-112 | 24VDC | White